TYPICAL TENDER SPECIFICATION

PART 1

Customer Document

PART 2

Standard Technical Specification

PART 2

Standby Diesel Generator

Standard Technical Specification

- General

The specification covers the supply, delivery, complete installation and commissioning on site in full working order of an emergency diesel generator to provide emergency electrical power for UPS systems, computer hardware, cooling systems and lighting.

Full particulars, performance curves and illustrations of the equipment offered must be submitted with the tender.  Tenderers may quote for their standard equipment complying with the specification and any deviation from the specification must be fully detailed.

The set shall be fully automatic i.e., shall start when any one phase of the mains supply fails and shall shut down when normal supply is re-established.  The set shall be capable of delivering the specified output continuously under the site conditions without overheating.

The client will provide a plant room for open sets or a concrete slab for enclosed sets as shown on the drawings included in the detailed specification.

Tenderers must confirm that the space is sufficient for the installation of the generator set, fuel tank and the control board and shall indicate the proposed layout of their equipment on the drawing in red ink.

The tenderer must furnish detailed description and illustration of the equipment offered and must complete the questionnaire following this specification.

Failure to submit any of the information asked for may disqualify the tenderer.

- Installation

Except for those items specifically excluded, tenderers must include for the complete installation and wiring of the plant in running order.

- Warning Notices

Tenderers must include in their tender for all notices that are required under the safety acts applicable to the area in which the installation is carried out.

4.	Drawings

The successful tenderer must, within two weeks after receipt of an order, submit detailed drawings and wiring diagrams of the plant and switchgear.

- Guarantee

The successful tenderer will be required to guarantee the complete plant for a period of 12 months from the date it has been taken over by the client in running order.

If during this period the plant is not in working order or not working satisfactorily owing to faulty material, design or workmanship, the contractor will be notified and immediate steps shall be taken by him to rectify the defects and/ or replace the affected parts on site, at his own expense.

- Operational Instruction

After completion of the installation and when the plant is in running order, the successful tenderer will be required to instruct an attendant in the operation of the plant, until he is fully conversant with the equipment and handling thereof.

Three copies of maintenance, fault–localizing and operating manuals are to be handed over to a representative of the client.

- Tests

Tests are to be carried out at the supplier’s premises, before the generating set is delivered to site, at which time a representative of the client will be present to ensure that the generating set complies with the specification and delivers the specified output.

- Engine

The engine must comply with the requirements laid down in SABS ISO 8528 and must be of a solid injection, compression ignition type, running at a speed not exceeding 1500rpm.  The engine must be amply rated for the required electrical output of the set, when running under the site conditions.  The starting period for either manual or automatic switching on until taking over the specified load by the generating set in two steps shall not exceed 20 seconds. The tenderer shall specify the initial one-step load capability of the generating set.

The engine shall be capable of delivering an output of 110% of specified output for one hour in any period of 12 hours consecutive running, in accordance with SABS ISO 8528.

Curves furnished by the engine maker, showing the output of the engine offered against the speed, for both intermittent and continuous operation, as well as fuel consumption figures must be submitted with the tender.

8.1	Lubrication

Lubrication of the main bearings and other important moving parts shall be a force-feed system.  An automatic low oil pressure cut out must be fitted, operating the stop solenoid on the engine and giving a visible and audible indication on the switchboard.

  - Fuel Pump

The fuel injection equipment must be suitable for operation with commercial brands of diesel fuel normally available in South Africa.

  - Cooling

The engine must be a water-cooled type, with a built-on heavy duty, tropical type radiator.

All air ducts for the cooling of the engine are to be allowed for.  The air shall not be allowed to re-circulate in the plant room and an air duct shall be supplied from the radiator face to discharge louvres in the plant room wall.

  - Governor

The speed of the engine shall be controlled by a governor in accordance with SABS ISO 8528 if not otherwise specified in the detail specification.  When the initial one step load is suddenly switched on or full load off the temporary speed variation shall not exceed 10%.  The permanent speed variation shall not exceed 1% of nominal engine speed.  The governor shall be electronic.

  - Derating

The engine must be derated for the site conditions as set out in the detail specification.

The derating of the engine shall be in accordance with the engine manufacturers derating curves. Copies of these derating curves or tables must be included with the tender response.

8.6	Starting and Stopping

The engine shall be easily started from cold, without the use of any special ignition devices, under summer as well as winter conditions.

Tenderers must state what arrangements are provided to ensure easy starting in cold weather.

The electrical circuits for heaters shall be taken from the control panel and must be protected by a suitable circuit breaker.

Besides the automatic starting and stopping, provision must be made on the control board for manual starting and stopping of the set.

The automatic control shall make provision for three consecutive starting attempts of 10 seconds with 10 second intervals.  Thereafter the set must be switched off and the start failure relay on the switchboard must give a visible and audible indication of the fault.

  - Starter Battery

The set must be supplied with a new fully charged maintenance free lead-calcium type battery.  The battery must have sufficient capacity to provide the starting torque stipulated by the engine maker, and for at least six consecutive starting attempts.  The battery must be housed on a suitable tray or stand.

  - Exhaust Silencer

It is essential to keep the noise level as low as possible.  An effective exhaust silencing system of the residential type is to be provided to limit the noise level to approximately 65/70/75dBA (select) @ 7 metres from the exhaust outlet or as specified in the detailed specification.

The exhaust pipe must be flexibly connected to the engine to take up vibrations transmitted from the engine, which may cause breakage.  The exhaust pipe and silencer inside the plant room must be lagged to reduce heat and noise transmission.

9.	Alternator

The alternator shall be of the self excited brushless type, with enclosed drip - proof housing, and must be capable of supplying the specified output continuously with a temperature rise not exceeding class H as laid down in SABS/ISO 8528 part 3 for rotor and stator windings.  The alternator shall be capable of delivering an output of 110% of the specified output for one hour in any period of 12 hours consecutive running.  Windings shall be fully impregnated for tropical climate and must have an oil resistant finishing varnish.

  - Alternator Protection

On the switchboard a multi-pole circuit breaker with instantaneous short circuit trips and thermal overload trips must be installed for protection of the alternator against short circuit and overload.

  - Regulation

The steady state voltage regulation must not exceed ± 1% of nominal voltage specified between no load and full load with the power factor between unity and 0.8 lagging and within the driving speed variation of 4.5%.

  - Performance

Following the application of 50/60/70% (select) of full load or the initial one step load capability of the engine, the transient voltage shall not exceed 15% and will recover to the nominal voltage within 500ms.

  - Output Voltage

The set shall have a site output as set out in the detail specification.

10.	Operation Selector

A four-position selector must be provided on the control panel marked “AUTO”, “MANUAL”.  “TEST” and “OFF”.

With the selector on “AUTO” the set shall automatically start and stop according to mains supply being available or not.

With the selector on “TEST” it shall be possible to start and stop the set with the push buttons but the running set shall not be switched to the load, UNLESS the mains supply fails during this test, in which case the set will be switched to the load.

With the selector on “MANUAL” the set must take load when started with the push button but it must not be possible to switch the set onto the mains or the mains onto the running set.

With the selector on ”OFF” the set shall be completely disconnected from automatic controls for cleaning and maintenance of the engine.

- By Pass Switch and Combined Mains Isolator (see detailed specification for requirement)

The switchboard must be equipped with a manually operated on-load by-pass switch, which shall either connect the incoming mains to the automatic control gear or directly to the outgoing feeder.  In the latter position the automatic control gear, including the Change-over gear shall be isolated for maintenance purposes.

It is required that the bypass switch isolator be mechanically isolated from the automatic control gear preferably in the lower portion of the switchboard cubicle.

- Battery Charging

Equipment must be provided on the switchboard for charging the battery from the utility supply. The charger shall be constant voltage, current limiting, operate automatically in accordance with the state of the battery and be capable of a continuous RMS current of at least 6 amps with an AC ripple content of less than 1% in order to prolong the life of the battery.

A flush mounted ammeter, suitably scaled, reading the charging current and a flush mounted voltmeter indicating the battery voltage must be provided on the switchboard.  An engine driven alternator must be provided for charging the battery during operation of the set.

13.	Starting and Stopping Delay

When the utility supply is interrupted on one or all phases, the voltage sensors shall initiate the starting cycle.  A 0-15 second’s adjustable start delay timer shall be provided to prevent start up on short power interruptions.

A stop delay timer is required to keep the set running for a period of 0-5 minutes, adjustable, after the main supply returns.  After changing back to the utility supply a 0-5 minute’s timer shall be provided to keep the set running for a cooling down period at no load before stopping.

- Mains Fail Simulation Key Switch

A main supply failure simulation key switch with TEST and NORMAL positions must be installed in the switchboard. In the TEST position, the set must be operated as if mains had failed, i.e. start and take load.

- Coupling

# The engine and alternator must be directly coupled by means of a high quality flexible coupling for double bearing alternators or a flexible plate supplied by the alternator manufacturer in the case of single bearing alternators.

- Fuel Tank

The tank shall have sufficient capacity to run the engine on full load for a period of (consultant to specify) hours, providing the following capacities are not exceeded: 200 litres for freestanding day tanks or 900 litres for set-mounted tanks. A 110% catch tank shall be installed under the fuel tank if floor standing or as required by local authorities.

The tank shall be fitted with a suitable filter, a full height protected sight glass calibrated in percentage, shut off valve and low level alarm at 30%, giving an audible and visible signal on the switchboard.

For sets rated at more than 100kVA an electrically operated pump with a suitable length of oil resistant hose must be supplied, for filling the fuel tank from 200 litre drums or as required by the detailed specification. For smaller sets a manually operated wing pump is to be supplied.

The inter-connecting fuel piping shall consist of black steel and connection to vibrating components shall be flexible tubing. A water trap shall be provided in the fuel pipeline between the tank and engine. A drain valve must be fitted to the underside of the fuel tank.

17.	Base Frame

The engine and the alternator of the set shall be built together on a common baseframe, of simplex/duplex type. For set mounted panels a Duplex frame will be preferred, consisting of a heavy duty inner frame on which the alternator and engine are secured with an outer floor standing frame between which purpose made anti-vibration mountings in “V” formation are mounted.  The Panel will be mounted on the floor standing frame.  The Simplex type baseframe will consist of a heavy-duty steel frame on which the alternator and engine are secured fitted with floor standing spring type anti-vibration mountings.  The set must be placed direct on the concrete floor.  A drip tray must be fitted under the engine.  The tray must be directly large enough to catch a drip from any part of the engine.

18.	Switchboard

A switchboard must be supplied for the set and is to incorporate all equipment necessary for control and protection of the generating set, the automatic change over and battery charging equipment.

The switchboard shall be a totally enclosed unit and shall consist of steel panels.

The steelwork of the boards must be thoroughly de-rusted, primed with zinc chromate and finished with two coats of signal red enamel or baked epoxy powder coating.

Suitable rated terminals must be provided for all circuits.  Where cable lugs are used, these shall be crimped.  Screwed terminals shall prevent spreading of the strands.

All wiring shall have each wire fitted with a cable or wire marker of approved type and the numbering of these markers must be shown on a wiring diagram of the switchboard.

The automatic control and protection control equipment shall be mounted on a separate easily replaceable small panel freely available in R.S.A. The automatic control shall be microprocessor based and shall be programmable, unless otherwise specified. The manufacturer shall guarantee the availability of compatible exchange control units for at least 10 years.

All equipment on the switchboard, such as contactors, isolators, busbars, etc. shall have ample current carrying capacity to continuously handle at least 110% of full load alternator current without overheating.

Wiring between hinged panels shall be in flexible lumes.

18.1	Earthing

An earthing bar must be fitted in the switchboard to which all non-current carrying metal parts shall be bonded.

The neutral point of the system must be solidly connected to this bar.  Suitable terminals must be provided on the earth bar for connection of the main earth conductors, which will be supplied and installed by others or as specified in the detailed specification.

18.2	The Following Equipment is Required in the Board

a)	One flush 96mm square dial voltmeter, scaled, reading the alternator voltage.

b)	One flush voltmeter selector switch with 6 metering and one off position, connecting the voltmeter to phase and neutral and phase to phase.

- One flush 96mm square dial indicating type frequency meter, indicating the alternator frequency.

- An hour meter with cyclometer counter, reading the number of hours the plant has been operating.  The smallest figure on this meter is to read 110th hour.

- One set of fuses or CB’s for potential circuits of the meters.

f)	Flush 96mm square dial maximum demand ammeters for measuring the alternator current, scaled to suit complete with necessary current transformer with resettable pointer.

g)	One isolator for the mains isolation (check detailed specification for requirement).

- Automatic – change over control equipment. (check detailed specification for requirements).

- One circuit breaker for alternator protection against overload and short circuit conditions (check detailed specification for requirement).

- One four-position operation selector switch.

- Two push buttons or one key switch marked “Start” and “Stop” for manual starting and stopping the set.

- Battery charging equipment as specified, complete with flush ammeter and voltmeter.

- Relays with re-set pushes as specified, for engine protection and warning.

- Fault indicating lights.

- Mains fail simulation key switch.

- Switch for fuel pump.

- Warning hooter.

- By pass switch.

- Test pushbutton to test all indicator lamps.

- Suitable terminals for incoming main and alternator cables, for the outgoing feeder and for the earth connection.

u)	Any other equipment necessary for the correct and safe operation of the installation.

18.3	Protection and Alarm Devices

Relays with reset push buttons are required to give a visible and audible signal and stop the engine when any of the protective devices operate.

Protection must be provided for high engine temperature, low lubrication oil pressure, overspeed/underspeed, start failure, low water level, overload, low fuel, battery charger fail, faulty switch position, emergency stop and abnormal voltage.

A potential free common alarm contact for remote monitoring must be supplied, unless otherwise specified in the detailed specification.

- Maintenance

The tender is inclusive of all breakdown maintenance, 24 hour emergency callout and four preventative maintenance visits during the first 12 months calculated on standby use of the generating set, excluding consumables such as oil and filters.  A fully priced pro-forma maintenance agreement must be submitted with the tender, catering for four preventative visits per annum and 24hour emergency callout facility. The number of bona-fide service technicians employed by the tenderer and stationed in Gauteng will be stated in the tender response.

PART 3

Detailed Technical Specification

PART 3

Detailed Technical Specification

1.	Site Information and Conditions

1.1	Location

  - Site Conditions

a)	Height above sea level: 	1680m

b)	Minimum ambient temperature:	-4 C

c)	Maximum ambient temperature:	+35 C

2.	Description of Load

The load shall consist of:-

a)	Rotary UPS Input power	880kW     1100kVA

100% One step load required. (ie)				880kWe

With 5% Voltage deviation during transient. 1% Frequency deviation during transient. This is not a misprint – this will supply the load if the Rotary UPS is out of Service or Fails.

3.	Output and Voltage

After the derating factors for the engine and generator due to site conditions have been taken into account, the set must have a continuous site output and voltage as follows: -

a)	Minimum continuous power output 	: 1100 kVA at power factor 0.8 lagging with an additional 10% overload available for one hour in every twelve.

b)	No load voltage	: 400/231 Volt  1%

c)		Nominal frequency	: 50Hz  1%

- Neutral solidly earthed.

4.	Alternator Rating

UPS load is 1100kVA/880kWe. The alternator shall be rated at a minimum of 1.7 x this UPS load, and not less than the overload capability of the engine.

5.	Switchboard / Control panel

All switch and control gear shall be rated for a fault current level of 30kA.  Tenderers shall submit type test certificates with their tender response proving IEC 60439-1 & IEC 61439-1 compliance with this requirement. The Standby Generator control panel shall include a changeover system that will allow no break mains return, peak lopping on demand, continues parallel with mains, mains failure detection in this mode without risk of tripping the genset breaker if mains fails.

- Installation

The successful tenderer will be responsible for the encapsulated Busbar/Power cable and control cable run between the alternator and Standby Generator Control panel.

- Sound Attenuation (if required)

Sound Attenuation on both the inlet and outlet air louvres and a high residential exhaust must be provided by the tenderer to achieve a level of approximately (select) dBA @ 7 metres measured outside the plant room in any direction. The tenderer shall indicate the dimensions of these sound attenuators in red ink on the plant room layout provided. The airflow through these attenuators shall not exceed 8 m/s and shall be well below the maximum static pressure restriction of the radiator airflow requirement of the engine manufacturer. The additional restriction of the inlet and outlet air weatherproof louvres will also be taken into account.

Tenderers shall submit detailed calculations showing engine manufacturers specified noise levels, insertion loss of the attenuators offered and resultant noise level.

- Drawings

The following drawings are included in the back of this specification document:

	Plant room layout

	Site plan

PART 4

Schedule of Information

PART 4

Schedule of Information

To be completed by Tenderers:

A)	Engine Information

| Item | Description of Engine |
| --- | --- |
| 1 | Manufacturers name ……..……………….. |
| 2 | Country of origin and year of manufacture ……………………… |
| 3 | Manufacturers type No. ……………………… |
| 4 | Continuous sea level rating after allowing for Ancillary equipment: ……………………… a) in b.h.p. ……………………… b) in kW ……………………… |
| 5 | Percentage derating for site conditions, in accordance with SABS ISO 8528 a) for altitude ……………………… b) for temperature ……………………… c) for humidity ……………………… d) Total derating ……………………… |
| 6 | Nett output on site in kW ……………………… |
| 7 | Nominal speed in r.p.m. ……………………… |
| 8 | Number of cylinders ……………………… |
| 9 | Strokes per working cycle …………………….... |
| 10 | Strokes in mm ……………………… |
| 11 | Initial one step load capability in kWe ……………………… |
| 12 | Cylinder bore in mm ……..……………….. |
| 13 | Swept volume in cm³ ……………………… |
| 14 | Mean piston speed in m/min ……………………… |
| 15 | Compression ratio ……………………… |
| 16 | Cyclic irregularity ……………………… |

A)	Engine Information (continued)

| Item | Description of Engine |
| --- | --- |
| 17 | Fuel consumption of the complete generating set on site in 1/h. “Load” is the specified nominal kWe rating : a) 100% load ……………………… b) 50% load ……………………… c) 25% load …………………….... NOTE: A tolerance of 5% shall be allowed above the stated value of fuel consumption. |
| 18 | Make of fuel injection system? …………………….... |
| 19 | Capacity of fuel tank in litre? ……………………… |
| 20 | Is gauge glass fitted to tank? ……………………… |
| 21 | What method for filling the fuel tank is included? ……………………… |
| 22 | Method of starting the engine ……………………… |
| 23 | Voltage of starting system ……………………… |
| 24 | Method of cooling? ……………………… |
| 25 | Type of radiator if water-cooled ……………………… |
| 26 | Type of heater for warming cylinder heads ……………………… |
| 27 | Capacity of water heater in kW ……………………… |
| 28 | Method of protection against high temperature ……………………… |
| 29 | Method of protection against low oil pressure ……..……………….. |
| 30 | Method of protection against low water level ……………………… |
| 31 | Type of governor ……………………… |
| 32 | Speed variation in % a) Temporary ……………………… b) Permanent ……………………… |
| 33 | Minimum time required for assumption of full load in seconds ……………………… |
| 34 | Recommended interval in running hours for: a) Lubricating oil change ……………………… b) Oil filter element change ……………………… c) Decarbonising …………………….… |
| 35 | Type of base offered ……………………… |

A)	Engine Information (continued)

| Item | Description of Engine |
| --- | --- |
| 36 | Can plant be placed on solid concrete floor? ……………………… |
| 37 | Are all accessories and ducts included? ……………………… |
| 38 | Is engine naturally aspirated? ……………………… |
| 39 | Are performance curves attached? ……………………… |
| 40 | Diameter of exhaust pipe ……………………… |
| 41 | Noise level at tail of exhaust pipe in dB (A) ……………………… |
| 42 | BMEP (4 stroke) at Continuous rating (kPa) ……………………… |
| 43 | % Load acceptance to SABS ISO 8528, with 10% transient speed variation ……………………… |

B)	Alternator Information

| Item | Description of Alternator |
| --- | --- |
| 1 | Manufacturers name ……..……………….. |
| 2 | Country of origin and year of manufacture ……………………… |
| 3 | Type of enclosure ……………………… |
| 4 | Normal speed in r.p.m. ……………………… |
| 5 | Terminal voltage ……………………… |
| 6 | Sea level rating kVA at 0.8 power factor ……………………… |
| 7 | Derating for site conditions in % …………………….... |
| 8 | Input required in kW for site kVA output required ……………………… |
| 9 | Method of excitation ……………………… |
| 10 | Efficiency at 0.8 p.f.: a) 100% load ……………………… b) 75% load ……………………… c) 50% load ……………………… |
| 11 | Maximum permanent voltage variation in % ……………………… |
| 12 | Transient voltage dip on full load application in % ……………………… |
| 13 | Voltage recovery on full load application in milli- seconds ……………………… |
| 14 | Is alternator brushless? ……………………… |
| 15 | Class of insulation of windings ……………………… |
| 16 | Is alternator tropicalised? ……………………… |
| 17 | Symmetrical short circuit current at terminals in Amps ……………………… |
| 18 | Type of coupling ……………………… |
| 19 | Number of bearings ……………………... |

C)	Switchboard / Control Panel Information

| Item | Description of Switchboard / Control Panel |
| --- | --- |
| 1 | Manufacturers name ……..……………….. |
| 2 | Country of origin ……………………… |
| 3 | Is board floor mounted? ……………………… |
| 4 | Finish of board ……………………… |
| 5 | Make of volt, amp, and frequency meters ……………………… |
| 6 | Sea level rating kVA at 0.8 power factor ……………………… |
| 7 | Scale range of voltmeters …………………….... |
| 8 | Scale range of ammeters ……………………… |
| 9 | Ratio of current transformers ……………………… |
| 10 | Make of hour meter ……………………… |
| 11 | Range of cyclometer ……………………… |
| 12 | Smallest unit shown on counter (Item 11) ……………………… |
| 13 | Make of circuit breaker ……………………… |
| 14 | Type of circuit breaker ……………………… |
| 15 | Rating of circuit breaker in Ampere and fault level in kA ……………………… |
| 16 | Setting range of overload trips ……………………… |
| 17 | Setting range of instantaneous trips ……………………… |
| 18 | Make of changeover equipment ……………………… |
| 19 | Make of voltage relay ……………………... |
| 20 | Is control and protection equipment mounted on a small removable panel ……………………… |
| 21 | Type of control equipment ……………………… |

D)	Dimension Information

| Item | Description of Dimensions |
| --- | --- |
| 1 | Overall dimensions of set in mm L =……… W =……… H =……… Panel if separate from genset L =……… W =……… H =……… |
| 2 | Is plant room adequate for the installation of the set and panel? ……………………… |
| 3 | Overall mass ……………………kg |

E)	Battery Information

| Item | Description of Batteries |
| --- | --- |
| 1 | Manufacturers name ……..……………….. |
| 2 | Country of origin ……………………… |
| 3 | Type of battery ……………………… |
| 4 | Voltage of battery ……………………… |
| 5 | Number of cells ……………………… |
| 6 | Capacity in A.h. ……………………… |
| 7 | Type of battery housing ……………………… |

F)	Deviations Information

Deviation from the Specification (State Briefly)

……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ………………………………………………………………………………………………………

G)	Guarantee Information

Guarantee

a) Guarantee in months……..……………………………………………………………… - State conditions of guarantee ……………………………………………………...…… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ………………………………………………………………………………………………………

- Delivery and Completion Time

Delivery Period and Installation

a) State no. of weeks required from date of order to complete set assembly, full factory testing and delivery to site of all equipment …………………… weeks b) Time required for complete installation and commissioning tests on site …………………… weeks TOTAL TIME REQUIRED FOR COMPLETION (a + b) …………………… weeks

I)	Spare Parts and Maintenance Facilities Information

Spare Parts and Maintenance Facilities

a) Approximate value of spares carried in stock for this particular diesel engine and alternator ……………………………………………………………………………………………………… b) Where are these spares held in stock? ……………………………………………………………………………………………………… c) What facilities exist for the servicing of equipment offered? ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… d) Where are these facilities available? ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ……………………………………………………………………………………………………… ………………………………………………………………………………………………………

PART 5

Price Schedule

PART 5

Price Schedule

  - Tender Price

The supply, delivery to site and complete installation in working order, of one emergency generating set with all accessories and switchgear, in accordance with the Specifications.

a) Local content	R……………………..

b) Imported content	R……………………..

c) Delivery and installation	R……………………..

SUB – TOTAL	R……………………..

Add 14% Value Added Tax	R……………………..

TOTAL FIRM TENDER PRICE	R……………………..

2.	Materials Offered Ex Import

1.	Type of equipment	: ___________________

2.	Country of origin	: ___________________

3.	Currency and official rate of exchange	: ___________________

4.	Date of exchange rate	: ___________________

5.	F.O.B or C.I.F value	: ___________________

Company stamp:

Name	_____________________	Signature:	____________________

Date: 	____________________

I/We tender for the execution of the service as described herein and in accordance with the Conditions contained in the specification, the documents specially mentioned therein, with the contents of which I/We acknowledge myself/ourselves to be fully acquainted.

TENDERER’S SIGNATURE	: ____________________

NAME OF SIGNATORY	: ____________________

TENDERER’S NAME	: ____________________

TENDERER’S ADDRESS	: ____________________

: ____________________

: ____________________

: ____________________

Date	: ____________________

PART 6

Drawings