## Summary
PROJECT: SANSA MATJIESFONTEIN BMS POINTS SCHEDULE
POINTS SUMMARY
DATA POINTS SCHEDULE |  |  |  |  | BMS I/O
BMS - Point Description | No | Description of Data Point | Unit | Function | [5 empty] | Description of Field Device / Interface | Field Device Supply By
|  | SUMMARY |  |  | QTY | DI | DO | AI | AO
| 1 | GENERATOR BUILDING AND SITE |  |  | 264 | 38 | 0 | 8 | 0
| 2 | MAIN OPERATIONS BUILDING |  |  | 133 | 54 | 3 | 0 | 0
| 3 | GATEHOUSE |  |  | 22 | 13 | 0 | 0 | 0
| 4 | LEGS ANTENNA |  |  | 8 | 13 | 3 | 0 | 0
|  | Points Total |  |  | 427 | 118 | 6 | 8 | 0
559

## Generator Building&Site
PROJECT: SANSA MATJIESFONTEIN BMS POINTS SCHEDULE
| FUNCTION |  |  | BMS I/O
| M | Monitor |  | AI | Analogue Input
| C | Control |  | AO | Analogue Output
| S | Status |  | DI | Digital Input
| A | Alarm |  | DO | Digital Output
| S/S | Start/Stop
| S/P | Set/Point
GENERATOR BUILDING AND SITE
DATA POINTS SCHEDULE |  |  |  |  | BMS I/O
BMS - Point Description | No | Description of Data Point | Unit | Function | [5 empty] | Description of Field Device / Interface | Field Device Supply By
| 1.1 | RMU-A |  |  | QTY | DI | DO | AI | AO
| 1.1.1 | NORMAL STATUS |  | S |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.1.2 | ABNORMAL STATUS |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.1.3 | OVERCURRENT |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.1.4 | CURRENT OVERLOAD TRIP |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.1.5 | EARTH FAULT TRIP |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
|  | Points per unit |  |  | 0 | 5 | 0 | 0 | 0
| 1.2 | RMU-B |  |  | QTY | DI | DO | AI | AO
| 1.2.1 | NORMAL STATUS |  | S |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.2.2 | ABNORMAL STATUS |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.2.3 | OVERCURRENT |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.2.4 | CURRENT OVERLOAD TRIP |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.2.5 | EARTH FAULT TRIP |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
|  | Points per unit |  |  | 0 | 5 | 0 | 0 | 0
| 1.3 | TRANSFORMER -A |  |  | QTY | DI | DO | AI | AO
| 1.3.1 | TEMPERATURE HIGH SET ALARM |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.3.2 | TEMPERATURE TRIP ALARM |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
|  | Points per unit |  |  | 0 | 2
| 1.4 | TRANSFORMER -B |  |  | QTY | DI | DO | AI | AO
| 1.4.1 | TEMPERATURE HIGH SET ALARM |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
| 1.4.2 | TEMPERATURE TRIP ALARM |  | A |  | 1 |  |  |  | BMS PLC | Terminal points provided by others
|  | Points per unit |  |  | 0 | 2 | 0 | 0 | 0
| 1.5 | GENERATOR-A (Analogue values) |  |  | QTY | DI | DO | AI | AO
| 1.5.1 | ENG TEMP VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.2 | OIL PRESSURE VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.3 | FUEL LEVEL VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.4 | FUEL LEVEL HEIGHT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.5 | FUEL CONSUMENED ON LAST RUN |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.6 | FUEL CONSUMPTION |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.7 | FUEL RUN TIME |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.8 | TOTAL HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.9 | HOURS FROM SERVICE |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.10 | SERVICE INTERVAL HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.11 | BATTERY AMPS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.12 | BATTERY VOLTS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.13 | %I1 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.14 | %I2 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.15 | %I3 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.16 | % KVA LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.17 | % KW Load |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.18 | HIGH FREQ SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.19 | LOW FREQ SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.20 | HIGH VOLTAGE SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.21 | LOW VOLTAGE SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.22 | KW ALARM POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.23 | KW SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.24 | DISPLAY TIME MINUTES |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.25 | DISPLAY TIME SECONDS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.26 | SESSION RUN TIME HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.27 | SESSION RUN TIME MINUTES |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.28 | STATUS WORDS MULTI STATE |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.29 | OPERATION BITS FOR MOTOR MIMIC |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.30 | ENGINE COOLING WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.31 | ENGINE COOLING WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.32 | ENGINE CHARGE AIR WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.33 | ENGINE CHARGE AIR WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.34 | ENGINE INTERCOOLER WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.35 | ENGINE INTERCOOLER WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.36 | ROOM TEMP 1 |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.37 | ROOM TEMP 2 |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.38 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.39 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.40 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.41 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
|  | Points per unit |  |  | 41 | 0 | 0 | 0 | 0
|  | GENERATOR-A (Binary values) |  |  | QTY | DI | DO | AI | AO
| 1.5.42 | AVAILABLE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.43 | NOT AVAILABLE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.44 | CRANKING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.45 | STARTED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.46 | NO LOAD READY |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.47 | ON LOAD RUN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.48 | LOAD TRANSFER IN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.49 | COOL DOWN RUN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.50 | TEST |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.51 | MANUAL |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.52 | CRANKING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.53 | STARTING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.54 | READY |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.55 | LEAD SET BLANK |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.56 | LEAD SET |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.57 | LAG SET |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.58 | GENERATOR OFF |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.59 | GENERATOR MANUAL |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.60 | GENERATOR AUTO |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.61 | GENERATOR TEST |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.62 | BC FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.63 | OVER VOLTAGE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.64 | UNDER VOLTAGE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.65 | OVER SPEED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.66 | UNDER SPEED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.67 | H.E.T. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.68 | L.O.P. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.69 | LOW ENGINE WATER LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.70 | START FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.71 | LOW FUEL LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.72 | LOW FUEL LEVEL SHUTDOWN |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.73 | k W OVERLOAD |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.74 | HIGH ALTERNATOR CURRENT |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.75 | REMOTE EMERGENCY OFF |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.76 | EMG STOP ENGINE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.77 | POWER METER FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.78 | DAY TANK LEVEL ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.79 | TEMP ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.80 | OIL PRESSURE ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.81 | PLC ERROR |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.82 | AUX SUPPLY A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.83 | AUX SUPPLY B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.84 | FUEL TRANSFER PUMP A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.85 | FUEL TRANSFER PUMP B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.86 | DAY TANK FILTER PUMP FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.87 | DAYTANK FILTER BLOCKED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.88 | BULKTANK FILTER PUMP FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.89 | BULKTANK FILTER BLOCKED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.90 | DAY TANK BUND FLOOD ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.91 | BULK TANK BUND FLOOD ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.92 | COMMS FAILED GENERATOR-C |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.93 | COMS FAILED SPS-C |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.94 | LOW INTER-COOLER WATER LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.95 | LOW COOLING TOWER WATER LEVEL ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.96 | LOW COOLING TOWER WATER LEVEL TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.97 | HET WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.98 | LOP WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.99 | H.I.T. WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.100 | H.I.T. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.101 | ENGINE OVER SPEED TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.102 | BULK TANK LEVEL ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.103 | CIRCUILATION PUMP A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.104 | CIRCUILATION PUMP B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.105 | ROOM FAN A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.106 | ROOM FAN B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.107 | PHASE ROTATION WRONG |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.108 | KVA OVER LOAD |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.5.109 | LOW STARTER BATERY VOLTAGE |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
|  | Points per unit |  |  | 68 | 0 | 0 | 0 | 0
GENERATOR - A DIESEL DAY TANK
|  | DAY FUEL TANK - GENERATOR A |  |  | QTY | DI | DO | AI | AO
| 1.5.110 | Daytank B Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.5.111 | Daytank B High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.5.112 | Daytank B Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
|  | Points per unit |  |  | 3 | 0 | 0 | 0 | 0 | Diesel Transfer System | BACnet/IP
Modbus RTU (deep Sea) | 1.6 | GENERATOR-B (Analogue values) |  |  | QTY | DI | DO | AI | AO
| 1.6.1 | ENG TEMP VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.2 | OIL PRESSURE VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.3 | FUEL LEVEL VAR |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.4 | FUEL LEVEL HEIGHT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.5 | FUEL CONSUMENED ON LAST RUN |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.6 | FUEL CONSUMPTION |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.7 | FUEL RUN TIME |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.8 | TOTAL HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.9 | HOURS FROM SERVICE |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.10 | SERVICE INTERVAL HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.11 | BATTERY AMPS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.12 | BATTERY VOLTS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.13 | %I1 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.14 | %I2 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.15 | %I3 LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.16 | % KVA LOAD |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.17 | % KW Load |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.18 | HIGH FREQ SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.19 | LOW FREQ SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.20 | HIGH VOLTAGE SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.21 | LOW VOLTAGE SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.22 | KW ALARM POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.23 | KW SET POINT |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.24 | DISPLAY TIME MINUTES |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.25 | DISPLAY TIME SECONDS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.26 | SESSION RUN TIME HOURS |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.27 | SESSION RUN TIME MINUTES |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.28 | STATUS WORDS MULTI STATE |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.29 | OPERATION BITS FOR MOTOR MIMIC |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.30 | ENGINE COOLING WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.31 | ENGINE COOLING WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.32 | ENGINE CHARGE AIR WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.33 | ENGINE CHARGE AIR WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.34 | ENGINE INTERCOOLER WATER OUTLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.35 | ENGINE INTERCOOLER WATER INLET TEMP |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.36 | ROOM TEMP 1 |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.37 | ROOM TEMP 2 |  | M | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.38 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.39 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.40 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.41 | ALARM BITS |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
|  | Points per unit |  |  | 41 | 0 | 0 | 0 | 0
|  | GENERATOR-B (Binary values) |  |  | QTY | DI | DO | AI | AO
| 1.6.42 | AVAILABLE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.43 | NOT AVAILABLE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.44 | CRANKING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.45 | STARTED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.46 | NO LOAD READY |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.47 | ON LOAD RUN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.48 | LOAD TRANSFER IN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.49 | COOL DOWN RUN |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.50 | TEST |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.51 | MANUAL |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.52 | CRANKING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.53 | STARTING |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.54 | READY |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.55 | LEAD SET BLANK |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.56 | LEAD SET |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.57 | LAG SET |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.58 | GENERATOR OFF |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.59 | GENERATOR MANUAL |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.60 | GENERATOR AUTO |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.61 | GENERATOR TEST |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.62 | BC FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.63 | OVER VOLTAGE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.64 | UNDER VOLTAGE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.65 | OVER SPEED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.66 | UNDER SPEED |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.67 | H.E.T. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.68 | L.O.P. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.69 | LOW ENGINE WATER LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.70 | START FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.71 | LOW FUEL LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.72 | LOW FUEL LEVEL SHUTDOWN |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.73 | k W OVERLOAD |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.74 | HIGH ALTERNATOR CURRENT |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.75 | REMOTE EMERGENCY OFF |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.76 | EMG STOP ENGINE |  | S | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.77 | POWER METER FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.78 | DAY TANK LEVEL ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.79 | TEMP ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.80 | OIL PRESSURE ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.81 | PLC ERROR |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.82 | AUX SUPPLY A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.83 | AUX SUPPLY B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.84 | FUEL TRANSFER PUMP A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.85 | FUEL TRANSFER PUMP B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.86 | DAY TANK FILTER PUMP FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.87 | DAYTANK FILTER BLOCKED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.88 | BULKTANK FILTER PUMP FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.89 | BULKTANK FILTER BLOCKED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.90 | DAY TANK BUND FLOOD ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.91 | BULK TANK BUND FLOOD ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.92 | COMMS FAILED GENERATOR-C |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.93 | COMS FAILED SPS-C |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.94 | LOW INTER-COOLER WATER LEVEL |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.95 | LOW COOLING TOWER WATER LEVEL ALARM |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.96 | LOW COOLING TOWER WATER LEVEL TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.97 | HET WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.98 | LOP WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.99 | H.I.T. WARNING |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.100 | H.I.T. TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.101 | ENGINE OVER SPEED TRIP |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.102 | BULK TANK LEVEL ANALOG FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.103 | CIRCUILATION PUMP A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.104 | CIRCUILATION PUMP B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.105 | ROOM FAN A FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.106 | ROOM FAN B FAILED |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.107 | PHASE ROTATION WRONG |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.108 | KVA OVER LOAD |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
| 1.6.109 | LOW STARTER BATERY VOLTAGE |  | A | 1 |  |  |  |  | Deep Sea -ModBus RTU | Monitored via Deapsee controller
|  | Points per unit |  |  | 68 | 0 | 0 | 0 | 0
GENERATOR - B DIESEL DAY TANK
|  | DAY FUEL TANK - GENERATOR B |  |  | QTY | DI | DO | AI | AO
| 1.6.110 | Daytank B Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.6.111 | Daytank B High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.6.112 | Daytank B Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
|  | Points per unit |  |  | 3 | 0 | 0 | 0 | 0 | Diesel Transfer System | BACnet/IP
| 1.7 | BULK DIESEL TANKS AND FUEL DELIVERY SYSTEM |  |  | QTY | DI | DO | AI | AO
| 1.7.1 | Bulk Tank 1 Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.2 | Bulk Tank 2 Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.3 | Bulk Tank 3 Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.4 | Bulk Tank 4 Level |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.5 | Bulk Tank 1 High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.6 | Bulk Tank 2 High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.7 | Bulk Tank 3 High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.8 | Bulk Tank 4 High Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.9 | Bulk Tank 1 Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.10 | Bulk Tank 2 Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.11 | Bulk Tank 3 Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.12 | Bulk Tank 4 Low Level Alarm |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.13 | Bulk Tank 1 FUEL FILTRATION QUANTITY |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.14 | Bulk Tank 1 FUEL FILTRATION RATE |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.15 | Bulk Tank 1 FUEL FILTER DIFFERENTIAL PRESS |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.16 | Bulk Tank 2 FUEL FILTRATION QUANTITY |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.17 | Bulk Tank 2 FUEL FILTRATION RATE |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.18 | Bulk Tank 2 FUEL FILTER DIFFERENTIAL PRESS |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.19 | Bulk Tank 3 FUEL FILTRATION QUANTITY |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.20 | Bulk Tank 3 FUEL FILTRATION RATE |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.21 | Bulk Tank 3 FUEL FILTER DIFFERENTIAL PRESS |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.22 | Bulk Tank 4 FUEL FILTRATION QUANTITY |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.23 | Bulk Tank 4 FUEL FILTRATION RATE |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.24 | Bulk Tank 4 FUEL FILTER DIFFERENTIAL PRESS |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.25 | Fuel transfer volume |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.26 | Fuel transfer rate |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.27 | Transfer pump panel activation from Generator run signal. |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.28 | Start stop of the transfer pump at pre-determined levels in the service tank. i.e. start pump at 50% and stop it at 80%. |  | M | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.29 | No flow on the pumps |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.30 | Emergency changeover of the pumps |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.31 | Fault reporting on non-operational pump. |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.32 | Filtration start stop programmed. |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.33 | Water in fuel detection |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.34 | No flow of the filtration pump |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.35 | Leak detection in the filtration set. |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.36 | Leak detection in the transfer pump set. |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.37 | The high level safety(Optical) that is hard wired to the transfer pump to prevent accidental overfill spillage. |  | A | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
| 1.7.38 | The fuel consumption of the generator will be done by two measuring the supply and return diesel flow rate and subtracting it, not sure where to report it to? |  | S | 1 |  |  |  |  | Diesel Transfer System | BACnet/IP
|  | Points per unit |  |  | 38 | 0 | 0 | 0 | 0
| 1.8 | MLV PANEL |  |  | QTY | DI | DO | AI | AO
| 1.8.1 | Generator A Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.2 | Generator A Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.3 | Generator B Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.4 | Generator B Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.5 | Generator C Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.6 | Generator C Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.7 | Generator D Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.8 | Generator D Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.9 | Generator E Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.10 | Generator E Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.11 | Generator F Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.12 | Generator F Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.13 | TX-A Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.14 | TX-A Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.15 | TX-B Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.16 | TX-B Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.17 | PV-A Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.18 | PV-A Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.19 | PV-B Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
| 1.8.20 | PV-B Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Generator Contractor
|  | Points per unit |  |  | 0 | 20 | 0 | 0 | 0
| 1.9 | Fire Detection |  |  | QTY | DI | DO | AI | AO
| 1.9.1 | Fire Panel - Common Fire |  | A | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
| 1.9.2 | Fire Panel - Common Fault |  | S | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
|  | Points per unit |  |  | 2 | 0 | 0 | 0 | 0
| 1.10 | HVAC and Wet Services |  |  | QTY | DI | DO | AI | AO
| 1.10.1 | Electrical MLV Substation Temperature |  | M |  |  |  | 1 |  | BMS PLC | Thermostat by BMS contractor
| 1.10.2 | Electrical MLV Substation Temperature - High level alarms |  | A |  | 1 |  |  |  | BMS PLC | Thermostat by BMS contractor
| 1.10.3 | Electrical Transformer Room Temperature |  | M |  |  |  | 1 |  | BMS PLC | Thermostat by BMS contractor
| 1.10.4 | Electrical Transformer Room Temperature - High level alarms |  | A |  | 1 |  |  |  | BMS PLC | Thermostat by BMS contractor
| 1.10.5 | Domestic Water Supply - Tank Level |  | M |  |  |  | 1 |  | BMS PLC | Level Sensor by BMS Contractor
| 1.10.6 | Domestic Water Supply - Tank High level alarm |  | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 1.10.7 | Domestic Water Supply - Tank Low level alarm |  | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
[5 empty] | 0 | 4 | 0 | 3 | 0
| 1.11 | HVAC and Wet Services |  |  | QTY | DI | DO | AI | AO
| 1.11.1 | Minisub 1 Low Voltage Monitoring |  | A |  |  |  | 1 |  | Voltage Monitoring with RF antenna | BMS contractor
| 1.11.2 | Minisub 2 Low Voltage Monitoring |  | A |  |  |  | 1 |  | Voltage Monitoring with RF antenna | BMS contractor
| 1.11.3 | Minisub 3 Low Voltage Monitoring |  | A |  |  |  | 1 |  | Voltage Monitoring with RF antenna | BMS contractor
| 1.11.4 | Minisub 4 Low Voltage Monitoring |  | A |  |  |  | 1 |  | Voltage Monitoring with RF antenna | BMS contractor
| 1.11.5 | Minisub 5 Low Voltage Monitoring |  | A |  |  |  | 1 |  | Voltage Monitoring with RF antenna | BMS contractor
[5 empty] | 0 | 0 | 0 | 5 | 0
TOTALS |  |  |  |  | QTY | DI | DO | AI | AO
[5 empty] | 264 | 38 | 0 | 8 | 0

## Main Building
PROJECT: SANSA MATJIESFONTEIN BMS POINTS SCHEDULE
| FUNCTION |  |  | BMS I/O
| M | Monitor |  | AI | Analogue Input
| C | Control |  | AO | Analogue Output
| S | Status |  | DI | Digital Input
| A | Alarm |  | DO | Digital Output
| S/S | Start/Stop
| S/P | Set/Point
MAIN OPERATIONS BUILDING
DATA POINTS SCHEDULE |  |  |  |  | BMS I/O
BMS - Point Description | No | Description of Data Point | Unit | Function | [5 empty] | Description of Field Device / Interface | Field Device Supply By
| 2.1 | SMDB-1 (BUILDING MDB) |  |  | QTY | DI | DO | AI | AO
| 2.1.1 | SMDB-1A Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.1.2 | SMDB-1A Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.1.3 | SMDB-1B Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.1.4 | SMDB-1B Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.1.5 | SMDB-1A Mains Voltage |  | A |  |  |  | 1 |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.1.6 | SMDB-1B Mains Voltage |  | A |  |  |  | 1 |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 0 | 4 | 0 | 0 | 0
| 2.2 | DB SANSA-A (SANSA EQUIPMENT ROOM) |  |  | QTY | DI | DO | AI | AO
| 2.2.1 | DB-SANSA-A Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.2 | DB-SANSA-A Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.3 | DB-SANSA-A UPS Section Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.4 | DB-SANSA-A UPS Section Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.5 | DB-SANSA-A UPS Section bypass Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.6 | DB-SANSA-A UPS Section bypass Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.7 | DB-SANSA-A Mains Voltage |  | A |  |  |  | 1 |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.2.8 | DB-SANSA-B Mains Voltage |  | A |  |  |  | 1 |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 0 | 6 | 0 | 0 | 0
| 2.3 | SANSA Equipment Room UPS |  |  | QTY | DI | DO | AI | AO
| 2.3.1 | UPS Common Alarm |  | A | 1 |  |  |  |  | ModBus RTU | UPS interface
| 2.3.2 | UPS Status Online/Bypass |  | S | 1 |  |  |  |  | ModBus RTU | UPS interface
| 2.3.3 | UPS Load persentage |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.4 | UPS Load - kW |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.5 | UPS Load - L1 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.6 | UPS Load - L2 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.7 | UPS Load - L3 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.8 | UPS Load - L1 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.9 | UPS Load - L2 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.10 | UPS Load - L3 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 2.3.11 | UPS Modbus Objects - Other |  | S | 30 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 40 | 0 | 0 | 0 | 0
| 2.4 | NASA DB MDP-A, MDP-B, DB-NER, DB-UPS-A, DB-UPS-B |  |  | QTY | DI | DO | AI | AO
| 2.4.1 | NASA MDP-A Mains A-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.2 | NASA MDP-A Mains A-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.3 | NASA MDP-A Mains B-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.4 | NASA MDP-A Mains B-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.5 | NASA MDP-B Mains A-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.6 | NASA MDP-B Mains A-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.7 | NASA MDP-B Mains B-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.8 | NASA MDP-B Mains B-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.9 | NASA DB-NER Mains A-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.10 | NASA DB-NER Mains A-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.11 | NASA DB-NER Mains B-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.12 | NASA DB-NER Mains B-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.13 | NASA DB-UPS-A Mains A-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.14 | NASA DB-UPS-A Mains A-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.15 | NASA DB-UPS-A Mains B-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.16 | NASA DB-UPS-A Mains B-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.17 | NASA DB-UPS-B Mains A-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.18 | NASA DB-UPS-B Mains A-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.19 | NASA DB-UPS-B Mains B-Supply Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.20 | NASA DB-UPS-B Mains B-Supply Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.21 | NASA MDP-A SPD Monitoring |  | M |  | 2 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.22 | NASA MDP-B SPD Monitoring |  | M |  | 2 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.23 | NASA DB-UPS-A SPD Monitoring |  | M |  | 2 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.24 | NASA DB-UPS-B SPD Monitoring |  | M |  | 2 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 2.4.25 | NASA DB-NER SPD Monitoring |  | M |  | 2 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 0 | 30 | 0 | 0 | 0
| 2.5 | NASA Equipment Room UPS-A |  |  | QTY | DI | DO | AI | AO
| 2.5.1 | UPS Common Alarm |  | A | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.2 | UPS Status Online/Bypass |  | S | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.3 | UPS Load persentage |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.4 | UPS Load - kW |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.5 | UPS Load - L1 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.6 | UPS Load - L2 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.7 | UPS Load - L3 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.8 | UPS Load - L1 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.9 | UPS Load - L2 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.10 | UPS Load - L3 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.5.11 | UPS Modbus Objects - Other |  | S | 10 |  |  |  |  | ModBus RTU | UPS interface supplied by others
|  | Points per unit |  |  | 20 | 0 | 0 | 0 | 0
| 2.6 | NASA Equipment Room UPS-B |  |  | QTY | DI | DO | AI | AO
| 2.6.1 | UPS Common Alarm |  | A | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.2 | UPS Status Online/Bypass |  | S | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.3 | UPS Load persentage |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.4 | UPS Load - kW |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.5 | UPS Load - L1 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.6 | UPS Load - L2 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.7 | UPS Load - L3 Amps |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.8 | UPS Load - L1 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.9 | UPS Load - L2 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.10 | UPS Load - L3 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | UPS interface supplied by others
| 2.6.11 | UPS Modbus Objects - Other |  | S | 10 |  |  |  |  | ModBus RTU | UPS interface supplied by others
|  | Points per unit |  |  | 20 | 0 | 0 | 0 | 0
| 2.7 | NASA Equipment and Control Room |  |  | QTY | DI | DO | AI | AO
| 2.7.1 | Water and Moisture Detection under Raised Floor - NASA Equipment room |  | A |  | 1 |  |  |  | BMS PLC | Sensor by BMS contractor
| 2.7.2 | Water and Moisture Detection under Raised Floor - NASA Control Room |  | A |  | 1 |  |  |  | BMS PLC | Sensor by BMS contractor
| 2.7.3 | VESDA Fire Detection - Common Fault |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
| 2.7.4 | VESDA Fire Detection - Pre-Alarm |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
| 2.7.5 | VESDA Fire Detection - Fire |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
| 2.7.6 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 2.7.7 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 2.7.8 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 2.7.9 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
| 2.7.10 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
| 2.7.11 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
|  | Points per unit |  |  | 3 | 5 | 3 | 0 | 0
| 2.8 | NASA Equipment and Control Room HVAC |  |  | QTY | DI | DO | AI | AO
|  | Monitor CRAC Unit 1 | [7 empty] | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.1 | Stop/Start | 0/1 | C | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.2 | Unit status | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.3 | Unit configuration (Master / Slave) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.4 | Supply air temperature setpoint | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.5 | Return air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.6 | Return air humidity | % RH | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.7 | Supply air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.8 | Filters dirty | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.9 | Unit common fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.10 | Fan Speed Actual | % | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.11 | Fan / airflow fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.12 | Fan Speed Control (dP / dT) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.13 | Fan dT Setpoint (use only if dT control) | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.14 | Fan dT Actual (use only if dT control) | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.15 | Unit Control (Local / Remote) | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
Monitor CRAC Unit 2
| 2.8.16 | Stop/Start | 0/1 | C | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.17 | Unit status | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.18 | Unit configuration (Master / Slave) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.19 | Supply air temperature setpoint | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.20 | Return air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.21 | Return air humidity | % RH | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.22 | Supply air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.23 | Filters dirty | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.24 | Unit common fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.25 | Fan Speed Actual | % | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.26 | Fan / airflow fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.27 | Fan Speed Control (dP / dT) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.28 | Fan dT Setpoint (use only if dT control) | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.29 | Fan dT Actual (use only if dT control) | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.30 | Unit Control (Local / Remote) | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
Monitor CRAC Unit 3
| 2.8.31 | Stop/Start | 0/1 | C | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.32 | Unit status | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.33 | Unit configuration (Master / Slave) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.34 | Supply air temperature setpoint | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.35 | Return air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.36 | Return air humidity | % RH | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.37 | Supply air temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.38 | Filters dirty | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.39 | Unit common fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.40 | Fan Speed Actual | % | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.41 | Fan / airflow fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.42 | Fan Speed Control (dP / dT) | 0/1 | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.43 | Fan dT Setpoint (use only if dT control) | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.44 | Fan dT Actual (use only if dT control) | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
| 2.8.45 | Unit Control (Local / Remote) | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | Connect to CRAC Unit interface
|  | Points per unit |  |  | 45 | 0 | 0 | 0 | 0
| 2.9 | SANSA Equipment and Operations Rooms |  |  | QTY | DI | DO | AI | AO
| 2.9.1 | VESDA Fire Detection - Common Fault |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
| 2.9.2 | VESDA Fire Detection - Pre-Alarm |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
| 2.9.3 | VESDA Fire Detection - Fire |  | A | 1 |  |  |  |  | BacNet IP | Interface with VESDA Detection Panel
|  | Points per unit |  |  | 3 | 0 | 0 | 0 | 0
| 2.10 | Fire Detection |  |  | QTY | DI | DO | AI | AO
| 2.10.1 | Fire Panel - Common Fire |  | A | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
| 2.10.2 | Fire Panel - Common Fault |  | S | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
|  | Points per unit |  |  | 2 | 0 | 0 | 0 | 0
| 2.11 | HVAC and Wet Services |  |  | QTY | DI | DO | AI | AO
| 2.11.1 | Domestic Water Supply - Tank Level |  | M |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.2 | Domestic Water Supply - Tank High level alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.3 | Domestic Water Supply - Tank Low level alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.4 | Domestic Water pressure | kPa | M |  | 1 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.5 | Booster pump status | 0/1 | S |  | 2 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.6 | Booster pump fault/trip | 0/1 | A |  | 2 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.7 | Continious Run / Water Leak Alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Booster pump control panel by Plumber
|  | Points per unit |  |  | 0 | 9 | 0 | 0 | 0
TOTALS |  |  |  |  | QTY | DI | DO | AI | AO
[5 empty] | 133 | 54 | 3 | 0 | 0

## Gatehouse
PROJECT: SANSA MATJIESFONTEIN BMS POINTS SCHEDULE
| FUNCTION |  |  | BMS I/O
| M | Monitor |  | AI | Analogue Input
| C | Control |  | AO | Analogue Output
| S | Status |  | DI | Digital Input
| A | Alarm |  | DO | Digital Output
| S/S | Start/Stop
| S/P | Set/Point
GATEHOUSE BUILDING
DATA POINTS SCHEDULE |  |  |  |  | BMS I/O
BMS - Point Description | No | Description of Data Point | Unit | Function | [5 empty] | Description of Field Device / Interface | Field Device Supply By
| 3.1 | DB-GH (GATEHOUSE MDB) |  |  | QTY | DI | DO | AI | AO
| 3.1.1 | DB-GH Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 3.1.2 | DB-GH Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 3.1.3 | DB-GH UPS Section Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 3.1.4 | DB-GH UPS Section Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 0 | 4 | 0 | 0 | 0
| 3.2 | Control Room UPS |  |  | QTY | DI | DO | AI | AO
| 3.2.1 | UPS Common Alarm |  | A | 1 |  |  |  |  | ModBus RTU | UPS interface
| 3.2.2 | UPS Status Online/Bypass |  | S | 1 |  |  |  |  | ModBus RTU | UPS interface
| 3.2.3 | UPS Load persentage |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.4 | UPS Load - kW |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.5 | UPS Load - L1 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.6 | UPS Load - L2 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.7 | UPS Load - L3 Amps |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.8 | UPS Load - L1 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.9 | UPS Load - L2 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.10 | UPS Load - L3 VL-N |  | M | 1 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
| 3.2.11 | UPS Modbus Objects - Other |  | S | 10 |  |  |  |  | ModBus RTU | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 20 | 0 | 0 | 0 | 0
| 3.3 | Fire Detection |  |  | QTY | DI | DO | AI | AO
| 3.3.1 | Fire Panel - Common Fire |  | A | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
| 3.3.2 | Fire Panel - Common Fault |  | S | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
|  | Points per unit |  |  | 2 | 0 | 0 | 0 | 0
| 2.11 | HVAC and Wet Services |  |  | QTY | DI | DO | AI | AO
| 2.11.1 | Domestic Water Supply - Tank Level |  | M |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.2 | Domestic Water Supply - Tank High level alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.3 | Domestic Water Supply - Tank Low level alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Level Sensor by BMS Contractor
| 2.11.4 | Domestic Water pressure | kPa | M |  | 1 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.5 | Booster pump status | 0/1 | S |  | 2 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.6 | Booster pump fault/trip | 0/1 | A |  | 2 |  |  |  | BMS PLC | Booster pump control panel by Plumber
| 2.11.7 | Continious Run / Water Leak Alarm | 0/1 | A |  | 1 |  |  |  | BMS PLC | Booster pump control panel by Plumber
|  | Points per unit |  |  | 0 | 9 | 0 | 0 | 0
TOTALS |  |  |  |  | QTY | DI | DO | AI | AO
[5 empty] | 22 | 13 | 0 | 0 | 0

## LEGS Antenna
PROJECT: SANSA MATJIESFONTEIN BMS POINTS SCHEDULE
| FUNCTION |  |  | BMS I/O
| M | Monitor |  | AI | Analogue Input
| C | Control |  | AO | Analogue Output
| S | Status |  | DI | Digital Input
| A | Alarm |  | DO | Digital Output
| S/S | Start/Stop
| S/P | Set/Point
LEGS ANTENNA
DATA POINTS SCHEDULE |  |  |  |  | BMS I/O
BMS - Point Description | No | Description of Data Point | Unit | Function | [5 empty] | Description of Field Device / Interface | Field Device Supply By
| 4.1 | DB-LEGS (GATEHOUSE MDB) |  |  | QTY | DI | DO | AI | AO
| 4.1.1 | DB-LEGS-A Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.2 | DB-LEGS-A Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.3 | DB-LEGS-B Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.4 | DB-LEGS-B Mains Circuit Breaker Trip |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.5 | DB-LEGS-UPS Mains Circuit Breaker On/Off |  | S |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.6 | DB-LEGS-UPS Mains Circuit Breaker On/Off |  | A |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.7 | DB-LEGS-A SPD Monitoring |  | M |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.8 | DB-LEGS-B SPD Monitoring |  | M |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
| 4.1.9 | DB-LEGS-UPS SPD Monitoring |  | M |  | 1 |  |  |  | BMS PLC | Hardwire to panel provided by Electrical Contractor
|  | Points per unit |  |  | 0 | 9 | 0 | 0 | 0
| 4.2 | LEGS Antenna |  |  | QTY | DI | DO | AI | AO
| 4.2.1 | Water and Moisture Detection |  | A |  | 1 |  |  |  | BMS PLC | Sensor by BMS contractor
| 4.2.2 | Fire Panel - Common Fire |  | A | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
| 4.2.3 | Fire Panel - Common Fault |  | S | 1 |  |  |  |  | BacNet IP | Advance Commander Fire Systems Contractor
| 4.2.4 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 4.2.5 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 4.2.6 | Digital Output - to be programmed |  | S/A |  |  | 1 |  |  | BMS PLC | Staus reporting to NASA
| 4.2.7 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
| 4.2.8 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
| 4.2.9 | Digital Input - to be programmed |  | S/A |  | 1 |  |  |  | BMS PLC | NASA Input
|  | Points per unit |  |  | 2 | 4 | 3 | 0 | 0
| 4.3 | LEGS Antenna HVAC |  |  | QTY | DI | DO | AI | AO
| 4.3.1 | Stop/Start |  |  | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
| 4.3.2 | No Units Running | 0/1 | S | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
| 4.3.3 | Common Fault | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
| 4.3.4 | Room Temperature Setpoint | °C | S/P | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
| 4.3.5 | Actual Room Temperature | °C | M | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
| 4.3.6 | High Room Temperature Alarm | 0/1 | A | 1 |  |  |  |  | HVAC BACnet/IP | AC Contractor
|  | Points per unit |  |  | 6 | 0 | 0 | 0 | 0
TOTALS |  |  |  |  | QTY | DI | DO | AI | AO
[5 empty] | 8 | 13 | 3 | 0 | 0

## Nasa (hidden)
Antenna
Main Building