## Index (hidden)
1 | BILL NO. 1
PRELIMINARIES AND GENERAL
2 | BILL NO. 2
LOW VOLTAGE INSTALLATION
3 | BILL NO. 3
MEDIUM VOLTAGE DISTRIBUTION SWITCHGEAR
4 | BILL NO. 4
POWER INSTALLATION FITTINGS AND ACCESSORIES
4.1 Warehouse
4.2 Office
4.3 DC Office
5 | BILL NO. 5
LIGHTING INSTALLATION FITTINGS AND ACCESSORIES
5.1 All Areas
5.2 Warehouse
5.3 Offices
5.4 DC Offices
BILL NO. 6
HVAC INSTALLATION
BILL NO. 7
FIRE DETECTION INSTALLATION
BILL NO. 8
PC SUMS

## PART C1.2.5 E & LP
SANSA MATJIESFONTEIN
ELECTRICAL INSTALLATION - EARTHING AND LIGHTNING PROTECTION INSTALLATION
PART C1.2.5
BILL OF QUANTITIES
[7 empty] | MAIN BUILDING | ENERGY CENTRE | GUARD HOUSE | SITE
ITEM | DESCRIPTION |  | UNIT | QTY | RATE | TOTAL | QTY | QTY | QTY | QTY
1.0 | BILL NO. 1
PRELIMINARIES AND GENERAL
CONDITIONS OF CONTRACT
Provisional and General items in order to comply with the Conditions of Contract associated with the works contained in this document.
1.1 | Test, Commission and prepare As-Built drawings |  | UNIT: Item; QTY: 1; TOTAL: 0
1.2 | Laminated drawings for all Plant rooms and Network rooms |  | UNIT: Item; QTY: 1; TOTAL: 0
1.3 | Insurances |  | UNIT: Item; QTY: 1; TOTAL: 0
1.4 | Mobilisation |  | UNIT: Item; QTY: 1; TOTAL: 0
1.5 | Project Management |  | UNIT: Item; QTY: 1; TOTAL: 0
1.6 | Site Tools and Instrumentation |  | UNIT: Item; QTY: 1; TOTAL: 0
1.7 | Maintenance and Guarantee for 12 months after practical completion |  | UNIT: Item; QTY: 1; TOTAL: 0
1.8 | Site Establishment |  | UNIT: Item; QTY: 1; TOTAL: 0
1.9 | Site Running Costs |  | UNIT: Item; QTY: 1; TOTAL: 0
1.10 | Demobilisation |  | UNIT: Item; QTY: 1; TOTAL: 0
1.11 | Vehicles |  | UNIT: Item; QTY: 1; TOTAL: 0
1.12 | Allowance to fix price for the duration of the contract |  | UNIT: Sum; QTY: 1; TOTAL: 0
The rates in the remainder of the Bill of Quantities (BOQ) must exclude these costs, as they are to be priced under this item.
1.13 | Remote Location Overhead Costs |  | UNIT: Sum; QTY: 1; TOTAL: 0
Provide a lump sum cost for all additional expenses associated with working at the remote project site, located approximately 230 km from Cape Town and 5 km south of Matjiesfontein. This includes transportation of materials and personnel, accommodation, site establishment, and any other costs related to the remote nature of the location. The rates in the remainder of the Bill of Quantities (BOQ) must exclude these costs, as they are to be priced under this item.
1.14 | OTHER ITEMS
Any other items tenderers may wish to add of a preliminary and general nature not specifically mentioned above in order to comply with the specification and contract conditions. Please add below:
1.14.1 |  |  | UNIT: Item; QTY: 1; TOTAL: 0
1.14.2 |  |  | UNIT: Item; QTY: 1; TOTAL: 0
1.14.3 |  |  | UNIT: Item; QTY: 1; TOTAL: 0
| TOTAL - BILL NO 1 CARRIED TO FINAL SUMMARY PAGE |  | TOTAL: 0
2.0 | BILL NO. 2
EARTHING & LIGHTNING PROTECTION
THE WORK DETAILED BELOW AS WELL AS IN ALL OF THE SUBSEQUENT BILLS IN THIS EARTHING AND LIGHTNING PROTECTION INSTALLATION IS FOR THE COMPLETE SUPPLY, DELIVERY ON SITE AND CONSTRUCTION OF THE FOLLOWING MATERIAL AND EQUIPMENT AND THE GUARANTEE THEREOF, AS SPECIFIED
All prices listed below must make provision for the delivery to site and must include all materials deemed necessary for commissioning of equipment in full, including all handling costs, insurance and any other costs involved in the delivery of material and equipment to complete installation.
Note: All material quantities are to be ordered according to drawings and not this BOQ
2.1.1 | Bonding of Structural Columns
Supply and install 50mm² steel earth strap from structural steel to 100x100x50 cast in earth test joint box with galvanised steel cover plate. Connect test joint box to 1500mm x 16mm earth spike via a 95mm² PVC insulated conductor. Earth spike to be driven into the ground to a depth of 1200mm or deeper.
Refer to the detail "TYPICAL DETAIL FOR BONDING COLUMN STEEL TO EARTH STRAP" on drawing J2700-001-EL-01 EARTHING AND LIGHTING PROTECTION LAYOUT.
| Supply |  | Each | 30 |  | 0 | 15 | 8 | 7
| Install |  | UNIT: Each; QTY: 30; TOTAL: 0
2.1.2 | Bonding of Roof Structure
Supply and install 50mm² steel earth strap from structural steel to 100x100x50 cast in earth test joint box with galvanised steel cover plate. Connect test joint box to roof structure via 70mm² ICEC.
Refer to the detail "TYPICAL LIGHTNING PROTECTION DRAWBOX DETAIL - BONDING TO ROOF" on drawing J2700-001-EL-01 EARTHING AND LIGHTING PROTECTION LAYOUT.
| Supply |  | Each | 14 |  | 0 | 10 | 0 | 4
| Install |  | UNIT: Each; QTY: 14; TOTAL: 0
2.2 | Supply and install 70mm² BCEC at 500mm below ground to connect all earth spikes. Include all terminations and trenching. All below ground terminations to be exothermically welded.
| Supply |  | m | 665 |  | 0 | 345 | 220 | 100
| Install |  | UNIT: m; QTY: 665; TOTAL: 0
| Termination |  | Each | 30 |  | 0 | 15 | 8 | 7
2.3 | Supply and install Earth Matt to achieve a <1ohm earth measurement. Earth matt tails to be connected to the earth bar in the location where it has been installed. All below ground terminations to be exothermically welded.
2.3.1 | Energy Centre - LV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.3.2 | Energy Centre - MV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.3.3 | Main Operations Building - LV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.3.4 | Gatehouse Building - LV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.3.5 | Minisub 1-5
| Supply |  | UNIT: Each; QTY: 5; TOTAL: 0; QTY: 5
| Install |  | UNIT: Each; QTY: 5; TOTAL: 0
2.4 | Supply and install Copper Earth Bar on insulators mounted on wall - 300mmx50mmx6mm
2.4.1 | Energy Centre - LV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.4.2 | Energy Centre - MV
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.4.3 | Main Operations Building - LV, NASA Equipment Room, SANSA Equipment Room
| Supply |  | UNIT: Each; QTY: 3; TOTAL: 0; QTY: 3
| Install |  | UNIT: Each; QTY: 3; TOTAL: 0
2.4.4 | Gatehouse
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
2.5 | 15m Lightning protection mast with own earth matt bonded to the structure earth. All below ground terminations to be exothermically welded.
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
| TOTAL - BILL NO 2 CARRIED TO FINAL SUMMARY PAGE |  | TOTAL: 0
3.0 | BILL NO. 3
NASA LEGS ANTENNA EARTHING AND LIGHTING PROTECTION
3.1 | Site
3.1.1 | IP54 Polycarbonate Kiosk with wooden backboard inclusive of 300mm x 50mm x 6mm copper earth bar mounted on insulators. Kiosk to be mounted on precast concrete plinth with sleeves for incoming cables.
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
3.1.2 | Earth Matt with <10 Ohm resistance. Earth matt tails to be connected to earth bar in kiosk. All below ground terminations to be exothermically welded.
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
3.1.3 | Supply and install 70mm² BCEC at 500mm below ground level from Minisub earth bar to kiosk Include all terminations and trenching. All below ground terminations to be exothermically welded.
| Supply |  | UNIT: m; QTY: 130; TOTAL: 0; QTY: 130
| Install |  | UNIT: m; QTY: 130; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 2; TOTAL: 0; QTY: 2
3.2 | Antenna Level 1
3.2.1 | Supply and install 120mm² BCEC at 500mm below ground level around antenna base and terminate to base structural steel. All below ground terminations to be exothermically welded.
| Supply |  | UNIT: m; QTY: 50; TOTAL: 0; QTY: 50
| Install |  | UNIT: m; QTY: 50; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 2; TOTAL: 0; QTY: 2
3.2.2 | Link ground earth conductur to level 3 via 120mm² BCEC and exothermic weld - allow 10m length of cable per point. All below ground terminations to be exothermically welded.
| Supply |  | UNIT: each; QTY: 4; TOTAL: 0; QTY: 4
| Install |  | UNIT: each; QTY: 4; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 8; TOTAL: 0; QTY: 8
3.2.3 | Ground Test Point. All below ground terminations to be exothermically weleded.
| Supply |  | UNIT: each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: each; QTY: 1; TOTAL: 0
3.2.1 | 600mm x 50mm x 6mm Copper earth bar mounted on insulators with connection to earth conductor
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 2; TOTAL: 0; QTY: 2
3.3 | Antenna Level 3
3.3.1 | Connect support ring to bonding conductor from 1st floor via 120mm² ICEC
Refer to the detail "CONCRETE TOWER SUPPORT RING CONNECTION" on drawing J2700-001-EL-01 EARTHING AND LIGHTING PROTECTION LAYOUT.
| Supply |  | UNIT: each; QTY: 4; TOTAL: 0; QTY: 4
| Install |  | UNIT: each; QTY: 4; TOTAL: 0
3.3.2 | 600mm x 50mm x 6mm Copper earth bar mounted on insulators with connection to earth conductor
| Supply |  | UNIT: Each; QTY: 1; TOTAL: 0; QTY: 1
| Install |  | UNIT: Each; QTY: 1; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 2; TOTAL: 0; QTY: 2
3.4 | Power Fence
3.4.1 | Supply and install 70mm² BCEC at 500mm below ground level and connect to powwer fence and antenna earth. All below ground terminations to be exothermically weleded.
| Supply |  | UNIT: m; QTY: 100; TOTAL: 0; QTY: 100
| Install |  | UNIT: m; QTY: 100; TOTAL: 0
| Termination |  | UNIT: Each; QTY: 2; TOTAL: 0; QTY: 2
| TOTAL - BILL NO 3 CARRIED TO FINAL SUMMARY PAGE |  | TOTAL: 0
BILL NO. 4
ADDITIONAL ITEMS
4.1 | Other items the tenderer may consider necessary to complete the installation
4.1.1 |  | Supply | UNIT: No; QTY: 1; TOTAL: 0
|  | Install | UNIT: No; QTY: 1; TOTAL: 0
4.1.2 |  | Supply | UNIT: No; QTY: 1; TOTAL: 0
|  | Install | UNIT: No; QTY: 1; TOTAL: 0
4.1.3 |  | Supply | UNIT: No; QTY: 1; TOTAL: 0
|  | Install | UNIT: No; QTY: 1; TOTAL: 0
| TOTAL - BILL NO 4 CARRIED TO FINAL SUMMARY PAGE |  | TOTAL: 0
FINAL SUMMARY PAGE
BILL NO. 1
| PRELIMINARIES AND GENERAL |  | TOTAL: 0
BILL NO. 2
| EARTHING & LIGHTNING PROTECTION |  | TOTAL: 0
BILL NO. 3
| NASA LEGS ANTENNA EARTHING AND LIGHTING PROTECTION |  | TOTAL: 0
BILL NO. 4
ADDITIONAL ITEMS
0
Any other items tenderers may wish to add of a Technical nature not specifically mentioned above in order to comply with the specification and contract conditions. Please add below:
| TOTAL CARRIED TO BILL NO. 16 ELECTRICAL INSTALLATION - EARTHING & LIGHTNING PROTECTION PART C1.2.5 |  | TOTAL: 0